## Body
MODBUS Protocol
1. Introduction
MODBUS MCCB Protocol
2. Physical Layer
⊙ Communication port : RS485
⊙ Asynchronous format : Each character is composed of 10 bit.
(1 start bit + 8 data bits + 1 stop bit)
⊙ Baud rate : 19200 bps
⊙ Data Bits : 8 bits
⊙ Parity : No parity
⊙ Stop Bits : 1 bits
⊙ Master-Slave method: Only master is qualified for requesting,
while slave delivers the requested data and response to the required performance according to inquiry.
3. Data Link Layer
⊙ if master delivers the request frame, slave does the response frame.
Each frame is differenciated by dead time.
General form to send and receive frames is as follows:
| DESCRIPTION |  | SIZE
| SLAVE ADDRESS |  | 1 byte
| FUNCTION CODE |  | 1 byte
| DATA |  | N byte
| CRC |  | 2 byte
| DEAD TIME |  | 3.5 bytes transmission time
| Master |  | Request | Response | Slave
| Slave address |  | Device Address | Device Address | Self-address
| Definition of slave action |  | Function Code | Function Code | Echo or MSB=1
| Additional information to perform the requested action |  | Data | Data | Requested data or exception code
| CRC |  | Error check | Error check | CRC
⊙ SLAVE ADDRESS
Valid slave device address range : 0~247 decimal
Slave device address range in practice : 1~32 decimal
If the range of slave device address of the requested frame by master is 0, it means that
master device bradcasts to all slaves.
In case that master requests to slave, fill the relative slave address in address field and send it.
If slave responses to master, fill its own adress in address field and send it.
⊙ FUNCTION CODE
Valid range : 1~255
normal : 1~127, error : 129 ~ 255(normal + 0x80)
It defines slave's requested action by master.
Slave enters the following.
In case of normal response: Echo the function code requested, as it stands.
In case of exceptjonal response: Set to 1 as MSB of the function code requested and fill it in.
⊙ DATA
Register address
Amount of items to be handled
The number of byte of actual data
⊙ CRC
Error checking method.
CRC-16
CRC Generation Function
unsigned short CRC16(puchMsg, usDataLen)
unsigned char *puchMsg ; /* message to calculate CRC upon */
unsigned short usDataLen ; /* quantity of bytes in message */
{
unsigned char uchCRCHi = 0xFF ; /* high byte of CRC initialized */
unsigned char uchCRCLo = 0xFF ; /* low byte of CRC initialized */
unsigned uIndex ; /* will index into CRC lookup table */
while (usDataLen––) /* pass through message buffer */
{
uIndex = uchCRCHi ^ *puchMsgg++ ; /* calculate the CRC */
uchCRCHi = uchCRCLo ^ auchCRCHi[uIndex} ;
uchCRCLo = auchCRCLo[uIndex] ;
}
return (uchCRCHi << 8 ¦ uchCRCLo) ;
}
⊙ DEAD TIME
Frame is completed only when it has silent interval more than 3.5 character time after receiving the last character.
1 character time is approximately 0.5ms since BPS is 19200
(700ms to1000ms is recommended for the interval of master's request.)
4. MODBUS Exception Codes
| code | Name
| 0x01 | ILLEGAL FUNCTION
| 0x02 | ILLEGAL DATA ADDRESS
| 0x03 | ILLEGAL DATA VALUE
| 0x04 | SLAVE DEVICE FAILURE
| 0x10 | No data for event/fault record
| 0x11 | SBO TIME OUT
| 0x12 | ILLEGAL ADU LENGTH
| 0x13 | LOCAL MODE
※ Electronic MCCB, in fact, covers only yellow-sectioned exceptional codes.

## Format detailed
Function Code | Name | Charact eristic | Type | RegisterAddress | Address | Format | Reference
0x03 | Read Holding Reg. | R | Io (ⅹIn) | 40001 | 40000 | F001 | Position of decimal rotary switch(1~9) ※See rotary switch value
|  |  | Ir (ⅹIo) |  |  | F001 | Position of decimal rotary switch(1~9)
|  |  | tr | 40002 | 40001 | F001 | Position of decimal rotary switch(1~9)
|  |  | Ii |  |  | F001 | Position of decimal rotary switch(1~9)
|  |  | tsd | 40003 | 40002 | F001 | Position of decimal rotary switch(1~9)
|  |  | Isd |  |  | F001 | Position of decimal rotary switch(1~9)
|  |  | Ig | 40004 | 40003 | F001 | Position of decimal rotary switch(1~9)
|  |  | tg |  |  | F001 | Position of decimal rotary switch(1~9)
|  |  | Ir | 40005 | 40004 | F002 | Current value on long-time setting
|  |  | Isd | 40006 | 40005 | F002 | Current value on short-time setting
|  |  | Ii | 40007 | 40006 | F002 | Instantaneous current value
|  |  | Ig | 40008 | 40007 | F002 | Current value on earth-fault setting(shows 0 at earth-fault-off)
|  |  | Imax Phase | 30001 | 30000 | F001 | The highest current value on R/S/T-phase and the phase's information(0~2)
|  |  | Display Mode |  |  | F001 | CT rating : 3P160, 3P250, 3P400, 3P630, 3P800, 4P160, 4P250, 4P400, 4P630, 4P800 (0~9)
|  |  | Trip Information | 30002 | 30001 | F003 | Resource of trip phase, trip
|  |  | State |  |  | F004 | ZSI information, ZSI input on short-time/earth-fault tripping, MCCB transmission
0x04 | Read Input Reg. | R Only | Ir | 30003 | 30002 | F002 | Effective current value on R-phase
|  |  | Is | 30004 | 30003 | F002 | Effective current value on S-phase
|  |  | It | 30005 | 30004 | F002 | Effective current value on T-phase
|  |  | In | 30006 | 30005 | F002 | Effective current value on N-phase
|  |  | Imax | 30007 | 30006 | F002 | The highest effective current value among R/S/T-phase
|  |  | Trip Current | 30008 | 30007 | F002 | Effective current value on tripping
F001
8Bit Unsigned Integer type
F002
16Bit Unsigned Integer type : Little Endian
F003
F001형식
F004
F001형식

## F003 & F004 detailed
Trip Information (F003)
Bit 7 | Bit6 | Bit5 | Bit4 | Bit3 | Bit2 | Bit1 | Bit0
Earth-fault tripping | Short-time tripping | Long-time tripping | Instantaneous tripping | N-phase tripping | T-phase tripping | S-phase tripping | R-phase tripping
Set a bit, out of bit 4 to 7, to 1 when trouble occurs. |  |  |  | Set a bit, out of bit 0 to 3, to 1 when trouble occurs. All bits show 0 when earth-fault occurs.
State (F004)
Bit 7 | Bit6 | Bit5 | Bit4 | Bit3 | Bit2 | Bit1 | Bit0
Reserved |  |  | ZSI signal 1 : yes 0 : no | ZSI function 1 : Enable 0 : Disable | ZSI signal when short-time/earth-fualt tripping | No signal when short-time/earth-fault tripping | 1 : No current 0 : Current-existence
Don't care |  |  | Value of ZSI DI signal | Set to 1 ot 0 if only ZSI Jump is inserted | Set one, out of bit 1 to 2, to 1 under the condition of ZSI operation. Beyond that set both to 0. |  | depends current input of R/S/T phase
※ after tripping, fault information such as state, trip current is cleard once making contact into MCCB, again.

## Rotary-switch-value
종류 | RegisterAddress | Address | Note
Io (ⅹIn) | 40001 | 40000 | 1-0.5 / 2-0.6 / 3-0.7 / 4-0.8 / 5-0.9 / 6-1.0 / 7-1.0 / 8-1.0 / 9-1.0
Ir (ⅹIo) |  |  | 1-0.8 / 2-0.85 / 3-0.9 / 4-0.95 / 5-1.0 / 6-1.0 / 7-1.0 / 8-1.0 / 9-1.0
tr | 40002 | 40001 | 1-2 / 2-4 / 3-6 / 4-8 / 5-12 / 6-12 / 7-12 / 8-12 / 9-12
Ii |  |  | 1-1.5 / 2-2 / 3-3 /4-4 / 5-5 / 6-6 / 7-8 / 8-10 / 9-11
tsd | 40003 | 40002 | 1-0.05(on) / 2-0.1(on) / 3-0.2(on) / 4-0.3(on) / 5-0.3(on) / 6-0.3(off) / 7-0.2(off) / 8-0.1(off) / 9-0.05(off)
Isd |  |  | 1-1.5 / 2-2 / 3-3 / 4-4 / 5-5 / 6-6 / 7-7 / 8-8 / 9-10
Ig | 40004 | 40003 | 1-0.2 / 2-0.3 / 3-0.4 / 4-0.5 / 5-0.6 / 6-0.7 / 7-0.8 / 8-1.0 / 9-off
tg |  |  | 1-0.1(on) / 2-0.2(on) / 3-0.3(on) / 4-0.4(on) / 5-0.4(on) / 6-0.4(off) / 7-0.3(off) / 8-0.2(off) / 9-0.1(off)

## Example
Examples
(1) 03(0x03) Read Holding Registers
Example of a Request/response to read registers 40001 … 40004 from slave device 1
Should rotary switch set to move from left to right/ top to bottom at interval of 1:
Request |  | Response
Field Name | (Hex) | Field Name | (Hex)
Slave Address | 0x01 | Slave Address | 0x01
Function | 0x03 | Function | 0x03
Starting Address Hi | 0x00 | Byte Count | 0x08
Starting Address Lo | 0x00 | Register value Lo(40001) | 0x01
Quantity of Inputs Hi | 0x00 | Register value Hi (40001) | 0x02
Quantity of Inputs Lo | 0x04 | Register value Lo(40002) | 0x05
CRC Lo | 0x44 | Register value Hi (40002) | 0x06
CRC Hi | 0x09 | Register value Lo(40003) | 0x07
|  | Register value Hi (40003) | 0x03
|  | Register value Lo(40004) | 0x04
|  | Register value Hi (40004) | 0x08
|  | CRC Lo | 0x0D
|  | CRC Hi | 0xFC
(2) 04(0x04) Read Input Registers
Example of a Request/response to read registers 30001 … 30007 from slave device 1
Request |  | Response
Field Name | (Hex) | Field Name | (Hex)
Slave Address | 0x01 | Slave Address | 0x01
Function | 0x04 | Function | 0x04
Starting Address Hi | 0x00 | Byte Count | 0x0E
Starting Address Lo | 0x00 | Register value Lo(30001) | 0x00
Quantity of Inputs Hi | 0x00 | Register value Hi (30001) | 0x00
Quantity of Inputs Lo | 0x07 | Register value Lo(30002) | 0x00
CRC Lo | 0xB1 | Register value Hi (30002) | 0x00
CRC Hi | 0xC8 | Register value Lo(30003) | 0x00
|  | Register value Hi (30003) | 0x00
|  | Register value Lo(30004) | 0x00
|  | Register value Hi (30004) | 0x00
|  | Register value Lo(30005) | 0x00
|  | Register value Hi (30005) | 0x00
|  | Register value Lo(30006) | 0x00
|  | Register value Hi (30006) | 0x04
|  | Register value Lo(30007) | 0x00
|  | Register value Hi (30007) | 0x00
|  | CRC Lo | 0xEC
|  | CRC Hi | 0xE6